## Slide 1
/ntpc1
/ntpcltd1
/ntpclimited
/Company/ntpc
/ntpclimited
Follow us on:
Green Hydrogen Blending in PNG (upto 8%) and Green Hydrogen based Microgrids in Himalayas
P Rahul | Sr. Manager | NTPC
NTPC Bhadla
NTPC Rojmal
NTPC Koldam
NTPC Fatehgarh
NTPC Simhadri Floating
NTPC140MW Bilhaur
NTPC Kawas Green Hydrogen Blending
NTPC Kayamkulam Floating

## Slide 2
Green Hydrogen Blending in PNG
First time upto 8% in the country

## Slide 3
1
3
System Performance
4
Objective and Features
2
Project Details
  Assessments
5
Learnings

## Slide 4: Need for Hydrogen Blending
Energy Security
Decarbonation

## Slide 5: Objectives
  Technical validation
    System Design
    Execution and Operation
  Safety requirements
    Standards & Regulations
  Understands the Impact of hydrogen blending
    Gas assessment
    Material structure assessment
  Understanding user’s concerns and perception
NTPC kawas Township, Surat, Gujarat
India’s 1st Green Hydrogen
Blending with Natural Gas
Notes: Features
  200 kg of CO2 eq / year can be mitigated
  Import substitution
  Decentralized decarbonization of gas-based end-use application

## Slide 6: Project Details
PNG Network : Gujarat Gas Limited Surat GA
Blending Level : H2 at 5-20% v/v
RE Power : Floating Solar (NTPC Kawas)
Household : 200 nos.
Electrolyzer : PEM (Min 1 nm3/hr.)
H2 storage : 13 nm3 (640 WL) at 30 bar(g)
H2 blending : Active and Monitor, PID c/v, H2 Analyzer
Safety Studies : HAZOP, HAC, QRA, EMERA
  Commissioned on 02nd Jan 2023
  Scheme

## Slide 7: Safety Provisions
Standards Compliance
Electrical: IS 5571, IS 3043, IP Std Compliance
Instrumentation & Control System : API RP, EN 334, EN 14382
Piping Standards: OISD 118, ASME B31.12 and B31.3, PNGRB T4S Guidelines
Storage Cylinder – PESO GCR 2016
Safety Valves : ASME UV stamped
Safety System
Provision of Active and Monitor Pressure regulator
Emergency Shutdown for overpressure protection and leakage detection
Online analyser (H2, NG, and blended gas) for feedback control & protection
Safe shutdown of system (in-case of power supply failure)
Gas detectors for H2 and NG at strategic locations
Safety devices (flame arrester) in all venting points

## Slide 8: System Performance
Chart: Natural Gas and Hydrogen Flow @ 5% H2 Blending

## Slide 9: Gas Assessment – Composition & Odourant
8
Analysis Result at 5% Hydrogen blending with PNG
Month | Ethyl Mercaptan (ppm) | 
Jun-23 (week) | Before blending | After blending
First | 2.3 | 2.2
Second | 2.2 | 2.2
Third | 2.3 | 2.3
Fourth | 2.4 | 2.4
Odourant Testing
Gas Composition
Odourant Dilution
Test (dummy) riser
Purpose : Composition (Homogeneity)
Frequency : Every Month
Samples : 3 Samples
(blending skid, highest, farthest)
Month | Sample location | Hydrogen %
Jul-23 | Blending | 5.03
 | Farthest | 4.9
 | Highest | 4.92
Aug-23 | Blending | 4.81
 | Farthest | 4.62
 | Highest | 4.69
Purpose : Dilution Effect
Frequency : Every blending level
Samples : 4 Samples
(once in a week)

## Slide 10: Material Assessment in PNG Network
9
Material | Test / Analysis | Inference
Galvanised pipe | Composition | No variation
 | Tensile test | No variation
 | Corrosion mapping | No adverse effects
 | Macro structure | No discontinuity
Rubber seal | Compatibility test | No adverse effects
Burner | Macro structure | No discontinuity
Polyethylene pipe | Corrosion mapping | No adverse effects
 | Macrostructure | No discontinuity
Galvanised
pipe
Burner
Polyethylene
Purpose : Composition (Homogeneity)
Frequency : Every 3 Month
Samples : Polyethylene, Galvanised pipe, Burner, Rubber seal
Microscopic

## Slide 11: Training and Consumer Survey
10

## Slide 12: Learnings
Outcomes
Fail Safe Design
Standardised technical Specifications
Checks during commissioning and operation
Evaluation and performance
Impact/Assessment of the PNG network
Optimization of economics
Risk Assessment & Mitigation
Let's drive sustainability together and create value for our business
Notes: AG&P – Obtained Geographical Authorisation from PNGRB for 3 districts in Kerala: Alappuzha, Kollam, Trivandrum

## Slide 13
1
3
About the High Altitude Project
4
About GH2 based Microgrids
2
Comparison vis a vis DG
  Monthly energy Profiles
5
Challenges in such projects
Green Hydrogen based Microgrid in the Himalayas

## Slide 14: Green Hydrogen based Microgrids
14
Self-sustaining standalone system
Cost of power supply
Resources required
No fuel logistics involved
Completely green
Suitable for off-grid/remote locations
Cost parity with diesel power
Few moving parts - low maintenance
Solar irradiance
Water for generation of hydrogen
No risk of diesel/kerosene price escalation for the next 25 years

## Slide 15: DG vs Green Hydrogen Microgrid
Diesel Generator
Expensive and Difficult Logistics of Fuel (Diesel) Price to increase in future years
High local Pollution, health issues for personnel
High Maintenance and replacements due to extreme weather
Increases crude imports
Cost of Electricity ~ ₹45-55/kwh
Green Hydrogen Microgrid
Self Sustaining – No Fuel required
Zero Emissions
Low Maintenance
Decreases crude imports (ATMANIRBHAR)
Cost of Electricity ₹50-55/kWh, levellised for next 25 years
15

## Slide 16: About the High Altitude Project
16
3.2 MW
1 MW PEM
200 kg H2 @ 250 Bar
0.3 MW/1.2 MWh
200 kW
Note: Due to high altitude the systems will be oversized accordingly, the above-mentioned values are minimum
Broad Schematic of the system

## Slide 17: Month-wise Daily Average Energy Profile
17

## Slide 18: Month-wise Daily Average Energy Profile
18

## Slide 19: Taking up the Challenge
Extreme Weather Conditions
Small Working window in the year
Derating of Fuel Cell due to High Altitude
Additional Logistics Cost
Additional Manpower cost
Thermal Management is the key

## Slide 20
/ntpc1
/ntpcltd1
/ntpclimited
/Company/ntpc
/ntpclimited
Follow us on:
Thank You
Website: www.ntpc.co.in
Migratory Birds at NTPC Dadri
NTPC Ramagundam

## Slide 21: Diesel Price trend in last 10 years
21
7.2% CAGR
Ref: mypetrolprice.com